Keyes Community Services District

Consumer Confidence Report –

2023

Este informe contiene información muy importante sobre su agua de potable.  Tradúzcalo o hable con alguien que lo entienda bien.

We are pleased to present to you this year`s Annual Quality Water Report. This report is designed to inform you about the quality water and services we deliver to you every day. Our constant goal is to provide you with a safe and dependable supply of drinking water. We want you to understand the efforts we make to continually improve the water treatment process and protect our water resources. We are committed to ensuring the quality of your water. Our water source consists of 4 groundwater wells. Well 7 is located at the south end of Hatch Park, Well 8 at 5536 9th Street, Well 9 at 5400 block of Faith Home Road and Well 10 at 4741 Lucinda Avenue.

We have a source water assessment plan available from our office that provides more information such as potential sources of contamination.

This report shows our water quality and what it means.

CONTACT INFORMATION:

If you have any questions about this report or concerning your water utility, please contact Michael Jones at (209) 668-8341.  We want our valued customers to be informed about their water utility. If you want to learn more, please attend any of our regularly scheduled meetings.

Meeting Location: Keyes CSD Board Room 5601 7th St.

Meeting Time: 1:00 P.M. on the 4th Tuesday of the month.

Keyes Community Services District routinely monitors for constituents in your drinking water according to Federal and State laws.  This table shows the results of our monitoring for the period of January 1st to December 31, 2023.  As water travels over the land or underground, it can pick up substances or contaminants such as microbes, inorganic and organic chemicals, and radioactive substances.  All drinking water, including bottled drinking water, may be reasonably expected to contain at least small amounts of some constituents.  It`s important to remember that the presence of these constituents does not necessarily pose a health risk.

DEFINITIONS:

In this table you will find many terms and abbreviations you might not be familiar with. To help you better understand these terms we`ve provided the following definitions:

Non-Detects (ND) - laboratory analysis indicates that the constituent is not present.

Parts per million (ppm) or Milligrams per liter (mg/l) - one part per million corresponds to one minute in two years or a single penny in $10,000.

Parts per billion (ppb) or Micrograms per liter - one part per billion corresponds to one minute in 2,000 years, or a single penny in $10,000,000.

Parts per trillion (ppt) or Nanograms per liter (nanograms/l) - one part per trillion corresponds to one minute in 2,000,000 years, or a single penny in $10,000,000,000.

Parts per quadrillion (ppq) or Picograms per liter (picograms/l) - one part per quadrillion corresponds to one minute in 2,000,000,000 years or one penny in $10,000,000,000,000.

Million Fibers per Liter (MFL) - million fibers per liter is a measure of the presence of asbestos fibers that are longer than 10 micrometers.

Nephelometric Turbidity Unit (NTU) - nephelometric turbidity unit is a measure of the clarity of water. Turbidity in excess of 5 NTU is just noticeable to the average person.

Variances & Exemptions (V&E) - State or EPA permission not to meet an MCL or a treatment technique under certain conditions. (Only systems with a variance or exemption are REQUIRED to include this definition.  In addition, it is REQUIRED to provide an explanation of the reasons for the variance or exemption, date issued, status or remediation.)

Action Level - the concentration of a contaminant which, if exceeded, triggers treatment or other requirements which a water system must follow.

Treatment Technique (TT) - (mandatory language) A treatment technique is a required process intended to reduce the level of a contaminant in drinking water.

Maximum Contaminant Level (MCL) - (mandatory language) The `Maximum Allowed` (MCL) is the highest level of a contaminant that is allowed in drinking water.  MCLs are set as close to the MCLGs as feasible using the best available treatment technology.

Maximum Contaminant Level Goal (MCLG) - (mandatory language) The `Goal`(MCLG) is the level of a contaminant in drinking water below which there is no known or expected risk to health.  MCLGs allow for a margin of safety.

Maximum Residual Disinfectant Level (MRDL) - (mandatory language) The highest level of a disinfectant allowed in drinking water.  There is convincing evidence that addition of a disinfectant is necessary for control of microbial contaminants.

Maximum Residual Disinfectant Level Goal (MRDLG) - (mandatory language) The level of a drinking water disinfectant below which there is no known or expected risk to health.  MRDLGs do not reflect the benefits of the use of disinfectants to control microbial contaminants.

| Table 1 – Sampling Results of Coliform Bacteria |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contaminant | Violation | Your Water | Range Of Detection | MCL | MCLG | Typical Source |
| Microorganisms |  |  |  |  |  |  |
| Total Coliforms (including fecal coliform and E. Coli) Collection Dates: 01/03/2023- 12/05/2023 | N | 0 | 0-1 | More than 1 sample in a month with a detection | 0 | Naturally present in the environment |

| Table 2 - Results of Lead and Copper |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Substance | Number of samples collected | 90th percentile level detected | No. sites exceeding Action Level (AL) | Action Level (AL) | PHG | Typical Source(s) when found in Drinking Water |
| Inorganic Chemicals |  |  |  |  |  |  |
| Lead (ppb) Collection Dates: 03/23/2023- 10/23/2023 | 80 | 0 | 0 | AL=15 | 0 | Corrosion of household plumbing systems, erosion of natural deposits |
| Unregulated Contaminants |  |  |  |  |  |  |
| Copper (ppm) Collection Dates: 03/23/2023- 10/23/2023 | 80 | 76.7 | 0 | AL=1.3 | 1.3 | Corrosion of household plumbing systems; erosion of natural deposits; leaching from wood preservatives |

| Table 3 - Results of Sodium and Hardness |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Contaminant | Violation | Your Water | Range Of Detection | MCL | MCLG | Typical Source(s) when found in Drinking Water |
| Secondary/GP |  |  |  |  |  |  |
| Sodium (ppm) Collection Dates: 10/26/2021- 05/30/2023 | N | 30 | 25-33 | None | None | Salt present in the water and is generally naturally occurring. |
| Total Hardness (ppm) (CaCO3) Collection Dates: 10/26/2021- 03/07/2023 | N | 90 | 52-120 | None | None | Sum of polyvalent cations present in the water, generally magnesium and calcium, and are usually naturally occurring. |

| Table 4 - Primary Drinking Water Standards |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Substance | Violation | Your Water | Range of Detection | MCL | PHG (MCLG) | Typical Source(s) when found in Drinking Water |
| Inorganic Chemicals |  |  |  |  |  |  |
| Arsenic (ppb) Collection Dates: 01/03/2023- 12/27/2023 | N | 7.4 | 6.15-10.8 | 10 | 0.004 | Erosion of natural deposits; runoff from orchards; runoff from glass and electronics production wastes |
| Fluoride (ppm) Collection Dates: 10/26/2021- 03/07/2023 | N | 0.12 | 0-0.18 | 2.0 | 4 | Erosion of natural deposits; water additive which promotes strong teeth; discharge from fertilizer and aluminum factories |
| Nitrate (ppm) (measured as Nitrogen) Collection Dates: 01/03/2023- 12/05/2023 | N | 2.98 | 0.79-10.2 | 10 | 10 | Runoff from fertilizer use; leaching from septic tanks, sewage; erosion of natural deposits |
| Nitrate+Nitrite (ppm) Collection Dates: 10/16/2018- 04/11/2023 | N | 5.24 | 0.77-9.9 | 10 |  | Runoff from fertilizer use; leaching from septic tanks, sewage; erosion of natural deposits |
| Regulated SOC |  |  |  |  |  |  |
| 1,2,3-Trichloropropane (ppb) Collection Dates: 01/18/2022- 10/03/2023 | Y | 0.027 | 0-0.1095 | 0.005 | 0.7 | Discharge from industrial and agricultural chemical factories; leaching from hazardous waste sites; used as cleaning and maintenance solvent, paint and varnish remover, and cleaning and degreasing agent; byproduct during the production of other compounds and pesticides. |

| Table 5 - Secondary Drinking Water Standards |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Substance | Violation | Your Water | Range of Detections | MCL | MCLG | Typical Source(s) when found in Drinking Water |
| Secondary/GP |  |  |  |  |  |  |
| Chloride Collection Dates: 10/26/2021- 03/07/2023 | N | 10.8 | 7.2-14 | 500 | N/A | Runoff and leaching from natural deposits; seawater influence. |
| Specific Conductance (E.C.) Collection Dates: 10/26/2021- 03/07/2023 | N | 310 | 250-400 | 1600 | N/A | Runoff and leaching from natural deposits; seawater influence. |
| Sulfate Collection Dates: 10/26/2021- 03/07/2023 | N | 6.3 | 3.1-15 | 500 | N/A | Substances that form ions when in water; industrial wastes |
| Total Disolved Solids (Total Filterable Residue @ 180 C (TDS)) Collection Dates: 10/26/2021- 05/30/2023 | N | 224 | 194-280 | 1000 | N/A | Runoff and leaching from natural deposits. |
| Turbidity Collection Dates: 10/26/2021- 05/30/2023 | N | 0.08 | 0-0.2 | 5 | N/A | Soil runoff |

| Table 6- Results for Chlorine Residuals |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Substance | Violation | Your Water | Range of Detections | MRDL | MRDLG | Typical Source |
| Disinfectant Residual |  |  |  |  |  |  |
| Chlorine Residual (ppm) (Chlorine - Free ) Collection Dates: 01/03/2023- 12/05/2023 | N | 0.45 | 0-0.55 | MRDL = 4 | MRDLG = 4 | Drinking water disinfectant added for treatment. |

HEALTH EFFECTS:

While your drinking water meets the federal and state standard for arsenic, it does contain low levels of arsenic.  The arsenic standard balances the current understanding of arsenic’s possible health effects against the cost of removing arsenic from drinking water.  The U.S. Environmental Protection Agency continues to research the health effects of low levels of arsenic, which is a mineral known to cause cancer in humans at high concentrations and is linked to other health effects such as skin damage and circulatory problems.

Infants below the age of six months who drink water containing nitrate in excess of the MCL could become seriously ill and, if untreated, may die. Symptoms include shortness of breath and blue-baby syndrome.

Some people who use water containing 1,2,3-trichloropropane in excess of the notification level over many years may have an increased risk of getting cancer, based on studies in laboratory animals.

EXPLANATIONS:

Table 4 shows that our system uncovered some problems this year.  The violation is for 1,2,3,-TCP and we are correcting this by installing GAC (Granular Activated Carbon) treatment. The district will be placing the treatment system on it’s property located at the South/East corner of Jennie and Brianna Avenue. The treatment system will treat water from Well 7 and 10 and include a connection to Well 8 if treatment is needed for that location in the future. Plans and specifications have been completed. Project began advertising on February 27, 2024, and a Pre-Bid meeting was held on March 12, 2024. On June 25, 2024, the bid was awarded to the contractor and the anticipated completion date is July of 2025.

Effective December 14, 2017 the federal 1,2,3, Trichloropropane (1,2,3, -TCP) MCL is 5 ppt. Wells 7 and 10 have exceeded the 5 ppt. Quarterly monitoring of the well water is required at these wells. Keyes CSD must provide public notification regarding the exceedance. The most recent public notification was mailed to our customers on March 26, 2024, and posted at the Keyes Community Services District Office. We have completed a feasibility study of remedial alternatives and are currently working on adding treatment systems to the wells to mitigate the problem of 1,2,3-TCP.

Some people who drink water containing arsenic in excess of the MCL over many years could experience skin damage or problems with their circulatory system and may have an increased risk of getting cancer.

Nitrate in drinking water at levels above 10 ppm is a health risk for infants of less than six months of age. High nitrate levels in drinking water can cause blue baby syndrome. Nitrate levels may rise quickly for short periods of time because of rainfall or agricultural activity. If you are caring for an infant, you should ask advice from your health care provider.

All sources of drinking water are subject to potential contamination by substances that are naturally occurring or man-made. These substances can be microbes, inorganic or organic chemicals and radioactive substances. All drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants.  The presence of contaminants does not necessarily indicate that the water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the Environmental Protection Agency`s Safe Drinking Water Hotline at 1-800-426-4791.

MCL`s are set at very stringent levels. The MCL`s are set such that out of every 10,000 or 1,000,000 people (depending upon how the MCL was developed) drinking 2 liters of water every day for a lifetime, only 1 of those people may experience the described health effect.

Total Coliform: The Total Coliform Rule requires water systems to meet a stricter limit for coliform bacteria. Coliform bacteria are usually harmless, but their presence in water can be an indication of disease-causing bacteria. When coliform bacteria are found, special follow-up tests are done to determine if harmful bacteria are present in the water supply. If this limit is exceeded, the water supplier must notify the public by newspaper, television or radio. To comply with the stricter regulation, we have increased the average amount of chlorine in the distribution system.

Nitrates: As a precaution we always notify physicians and health care providers in this area if there is ever a higher than normal level of nitrates in the water supply.

If present, elevated levels of lead can cause serious health problems, especially for pregnant women and young children.  Lead in drinking water is primarily from materials and components associated with service lines and home plumbing.  Keyes Community Services District is responsible for providing high quality drinking water, but cannot control the variety of materials used in plumbing components.  When your water has been sitting for several hours, you can minimize the potential for lead exposure by flushing your tap for 30 seconds to 2 minutes before using water for drinking or cooking.  If you are concerned about lead in your water, you may wish to have your water tested.  Information on lead in drinking water, testing methods, and steps you can take to minimize exposure is available from the Safe Drinking Water Hotline or at http://www.epa.gov/safewater/lead. In our continuing efforts to maintain a safe and dependable water supply it may be necessary to make improvements in your water system.  The costs of these improvements may be reflected in the rate structure. Rate adjustments may be necessary in order to address these improvements.  Thank you for allowing us to continue providing your family with clean, quality water this year.  In order to maintain a safe and dependable water supply we sometimes need to make improvements that will benefit all of our customers. These improvements are sometimes reflected as rate structure adjustments. Thank you for understanding. Some people may be more vulnerable to contaminants in drinking water than the general population. Immuno-compromised persons such as persons with cancer undergoing chemotherapy, persons who have undergone organ transplants, people with HIV/AIDS or other immune system disorders, some elderly, and infants can be particularly at risk from infections. These people should seek advice about drinking water from their health care providers. EPA/CDC guidelines on appropriate means to lessen the risk of infection by cryptosporidium and other microbiological contaminants are available from the Safe Drinking Water Hotline (800-426-4791).

Please call our office if you have questions. We at Keyes Community Services District work around the clock to provide top quality water to every tap. We ask that all our customers help us protect our water sources, which are the heart of our community, our way of life and our children’s future.